{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":32,"n_cols":7,"rows_kept":32,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","2MXM-M9"]
[]
[]
[]
[]
["","","","","","2MXM50M3V1B9","2MXM50M2V1B9"]
["Dimensionet","Njësia","","Lartësia","mm","550","550"]
["","","","Gjerësia","mm","765","765"]
["","","","Thellësia","mm","285","285"]
["Pesha","Njësia","","","kg","41","41"]
["Motori i ventilatorit","Shpejtësia","Ftohje","Super e ulët","rpm","500","500"]
["","","Ngrohje","Super e ulët","rpm","500","500"]
["Kompresori","Type","","","","Kompresor rrotullues i mbyllur hermetikisht","Kompresor rrotullues i mbyllur hermetikisht"]
["Niveli i presionit të zhurmës","Ftohje","","Niveli i presionit të zhurmës-=-Ftohje-=-I lartë-=-dBA","dBA","48","48"]
["","Ngrohje","","I lartë","dBA","50","50"]
["Agjenti ftohës","Lloji","","","","R-32","R-32"]
["","Mbushja","","","kg","1.15","1.15"]
["","Mbushja","","","tCO2Eq","0.78","0.8"]
["","GWP","","","","675","675.0"]
["Lidhjet e tubacioneve","Gjatësia e tubacioneve","Maks.","OU - IU","m","","20"]
["","Mbushje shtesë me agjent ftohës","","","kg/m","0.02 (për gjatësinë e tubave që kalojnë 20m)","0.02 (për gjatësinë e tubave që kalojnë 20m)"]
["","Ndryshimi i nivelit","IU - OU","Maks.","m","15.0","15.0"]
["","","IU - IU","Maks.","m","7.5","7.5"]
["","Gjatësia totale e tubacioneve","Sistemi","Aktuale","m","30","30"]
["Aksesore Standarde","Installation manual","","","","1","1"]
["","Drain plug","","","","1","1"]
["","Reducer assembly","","","","1","1"]
["","Screw bag","","","","1","1"]
["Furnizimi me energji","Faza","","","","1~","1~"]
["","Frekuenca","","","Hz","50","50"]
["","Tensioni","","","V","220-230-240","220-230-240"]
["Shënime","","","","","(1) - Për një dhomë","(1) - Çdo D-AHU Professional mund të projektohet sipas nevojave tuaja. Zgjidhni njësinë tuaj për trajtimin e ajrit në tools.daikinapplied.eu"]