{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":47,"n_cols":8,"rows_kept":47,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","AZAS-MY1"]
[]
[]
[]
[]
["","","","","","AZAS100M7Y1B","AZAS125M7Y1B","AZAS140M7Y1B"]
["Dimensionet","Njësia","","Lartësia","mm","990","990","990"]
["","","","Gjerësia","mm","940","940","940"]
["","","","Thellësia","mm","320","320","320"]
["Pesha","Njësia","","","kg","","70"]
["Kompresori","Type","","","","","Kompresor rrotullues i mbyllur hermetikisht"]
["Diapazoni i funksionimit","Ftohje","Ambienti","Min.","°CDB","-5","-5","-5"]
["","","","Maks.","°CDB","46","46","46"]
["","Ngrohje","Ambienti","Min.","°C WB","-15","-15","-15"]
["","","","Maks.","°C WB","15.5","15.5","15.5"]
["Niveli i fuqisë së zhurmës","Ftohje","","","dBA","70","71","73"]
["","Ngrohje","","","dBA","","71","73 (1)"]
["Niveli i presionit të zhurmës","Ftohje","","Nom.","dBA","53","53","54"]
["","Ngrohje","","Nom.","dBA","57","57","57"]
["Agjenti ftohës","Lloji","","","","R-32","R-32","R-32"]
["","Agjenti ftohës-=-Ngarkesa-=-kg","","","kg","","2.60"]
["Antipiretik","GWP","","","","","675"]
["Agjenti ftohës","Mbushja","","","tCO2Eq","1.76","1.76","1.96"]
["Lidhjet e tubacioneve","Lëngu","","Dia. jasht.","mm","9.52","9.52","9.52"]
["Lidhjet e tubacioneve","Gas","","Diametri i jashtëm","mm","","15.9"]
["Lidhjet e tubacioneve","Gjatësia e tubacioneve","Maks.","OU - IU","m","30","30","30"]
["","","Sistemi","Ekuivalent","m","50","50","50"]
["","","","Pa ngarkesë","m","30","30","30"]
["","Mbushje shtesë me agjent ftohës","","","kg/m","Shihni manualin e instalimit","Shihni manualin e instalimit","Shihni manualin e instalimit"]
["","Ndryshimi i nivelit","IU - OU","Maks.","m","30.0","30.0","30.0"]
["","","IU - IU","Maks.","m","0.5","0.5","0.5"]
["Aksesore Standarde","Installation manual","","","","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1"]
["","General safety precautions","","","","1","1","1"]
["","LOT10 Energy Label","","","","1","1","1"]
["","Tie-wraps","","","","2","2","2"]
["Furnizimi me energji","Faza","","","","3~","3~","3~"]
["","Furnizimi me energji-=-Frekuenca","","Frekuenca","","50","50","50"]
["","Furnizimi me energji-=-Tensioni","","Tensioni","","380-415","380-415","380-415"]
["Rryma - 50Hz","Rryma - 50Hz-=-Amperët maksimalë të siguresës (MFA)","","Rryma - 50Hz-=-Amperët maksimalë të siguresës (MFA)-=-A","","","16"]
["Shënime","","","","","","(1) - Sipas ENER Lot 21","(1) - Sipas ENER Lot 21"]
["Pesha","Njësia","","","kg","70","","77"]
["Kompresori","Lloji","","","","Kompresor rrotullues i mbyllur hermetikisht","","Kompresor rrotullues i mbyllur hermetikisht"]
["Agjenti ftohës","Mbushja","","","kg","2.60","","2.90"]
["","GWP","","","","675","","675"]
["Lidhjet e tubacioneve","Gazi","","Dia. jasht.","mm","15.9","","15.9"]
["Rryma - 50 Hz","Amperët maksimalë të siguresës (MFA)","","","A","16","","16"]