{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":60,"n_cols":9,"rows_kept":60,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYA-DW1P-H-"]
[]
[]
[]
[]
["","","","","","EWYA009DAW1P-H-","EWYA011DAW1P-H-","EWYA014DAW1P-H-","EWYA016DAW1P-H-"]
["Niveli i presionit të zhurmës","Ftohje","","Nom.","dBA","44.0","47.7","50.8","51.0"]
["Komponentët hidraulikë","Ena e zgjerimit","","Vëllimi","l","8","8","8","8"]
["Gama e funksionimit","Ana e ajrit","Ftohje","Min.","°CDB","10","10","10","10"]
["","","","Maks.","°CDB","43","43","43","43"]
["","","Ngrohje","Maks.","°CDB","25","25","25","25"]
["","","","Min.","°CDB","-25","-25","-25","-25"]
["","Ana e ujit","Ngrohje","Min.","°CDB","9 (7)","9 (7)","9 (7)","9 (7)"]
["","","","Maks.","°CDB","60 (7)","60 (7)","60 (7)","60 (7)"]
["","","Ftohje","Maks.","°CDB","22","22","22","22"]
["","","","Min.","°CDB","5","5","5","5"]
["Mbushja e agjentit ftohës","Për qark","","","kg","3.80","3.80","3.80","3.80"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","2.6","2.6","2.6","2.6"]
["Kompresori","Type","","","","Kompresor rrotullues inverter i mbyllur hermetikisht","Kompresor rrotullues inverter i mbyllur hermetikisht","Kompresor rrotullues inverter i mbyllur hermetikisht","Kompresor rrotullues inverter i mbyllur hermetikisht"]
["","Starting method","","","","Drejtuar me inverter","Drejtuar me inverter","Drejtuar me inverter","Drejtuar me inverter"]
["","Sasia","","","","1","1","1","1"]
["Shkëmbyesi i nxehtësisë së ajrit","Lloji","","","","Fletë me efikasitet të lartë dhe lloji i tubit me nën-ngrohës të integruar","Fletë me efikasitet të lartë dhe lloji i tubit me nën-ngrohës të integruar","Fletë me efikasitet të lartë dhe lloji i tubit me nën-ngrohës të integruar","Fletë me efikasitet të lartë dhe lloji i tubit me nën-ngrohës të integruar"]
["Weight","Njësia","","","kg","147","147","147","147"]
["EER","","","","","3.35 (1), 5.34 (2)","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["Agjenti ftohës","GWP","","","","675.0","675.0","675.0","675.0"]
["","Lloji","","","","R-32","R-32","R-32","R-32"]
["","Qarqet","","Sasia","","1","1","1","1"]
["","Kontrolli","","","","Valvula elektronike e zgjerimit","Valvula elektronike e zgjerimit","Valvula elektronike e zgjerimit","Valvula elektronike e zgjerimit"]
["Motori i ventilatorit","Shpejtësia","Ftohje","Nom.","rpm","500","550","650","650"]
["","","Ngrohje","Nom.","rpm","400","450","550","650"]
["Kapaciteti ftohës","Nom.","","","kW","9.35 (1), 9.10 (2)","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Shkëmbyesi i nxehtësisë së ujit","Vëllimi i ujit","","","l","2","2","2","2"]
["","Vëllimi minimal i ujit në sistem","","","l","50 (6)","50 (6)","50 (6)","50 (6)"]
["","Lloji","","","","Shkëmbyesi i nxehtësisë së pllakës","Shkëmbyesi i nxehtësisë së pllakës","Shkëmbyesi i nxehtësisë së pllakës","Shkëmbyesi i nxehtësisë së pllakës"]
["Fuqia në hyrje","Ftohje","","Nom.","kW","2.79 (1), 1.71 (2)","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["","Ngrohje","","Nom.","kW","1.91 (3), 2.43 (4)","2.18 (3), 2.68 (4)","2.46 (3), 3.42 (4)","3.53 (3), 4.56 (4)"]
["Niveli i fuqisë së zhurmës","Ftohje","","Nom.","dBA","65.5","67.0","69.0","69.0"]
["COP","","","","","4.91 (3), 3.71 (4)","4.83 (3), 3.66 (4)","4.87 (3), 3.64 (4)","4.53 (3), 3.51 (4)"]
["Dimensionet","Njësia","","Gjerësia","mm","1,380","1,380","1,380","1,380"]
["","","","Thellësia","mm","460","460","460","460"]
["","","","Lartësia","mm","870","870","870","870"]
["Kontrolli i kapacitetit","Metoda","","","","E ndryshueshme (inverter)","E ndryshueshme (inverter)","E ndryshueshme (inverter)","E ndryshueshme (inverter)"]
["Ngrohja e ambientit","Dalja e ujit për klimë mesatare 55°C","Të përgjithshme","Seasonal space heating eff. class","","A++","A++","A++","A++"]
["","","","ηs (Efikasiteti sezonal i ngrohjes së ambientit)","%","135","132","134","132"]
["","","","SCOP","","3.44","3.37","3.42","3.37"]
["Ventilatori","Niveli i qarkullimit të ajrit","Ngrohje","Nom.","m³/min","48.0","55.8","70.4","85.0"]
["","","Ftohje","Nom.","m³/min","63","70","85","85"]
["Kapaciteti ngrohës","Nom.","","","kW","9.37 (3), 9.00 (4)","10.6 (3), 9.82 (4)","12.0 (3), 12.5 (4)","16.0 (3), 16.0 (4)"]
["Kompresori","Starting method","","","","Inverteri","Inverteri","Inverteri","Inverteri"]
["Power supply","Faza","","","","3~","3~","3~","3~"]
["","Frekuenca","","","Hz","50","50","50","50"]
["","Emri","","","","W1","W1","W1","W1"]
["","Tensioni","","","V","400","400","400","400"]
["Shënime","","","","","(1) - Ftohje: EW 12°C; LW 7°C; kushtet e ambientit: 35°CDB","(1) - Ftohje: EW 12°C; LW 7°C; kushtet e ambientit: 35°CDB","(1) - Ftohje: EW 12°C; LW 7°C; kushtet e ambientit: 35°CDB","(1) - Ftohje: EW 12°C; LW 7°C; kushtet e ambientit: 35°CDB"]
["","","","","","(2) - Ftohje: EW 23℃; LW 18℃; kushtet e ambientit: 35°CDB","(2) - Ftohje: EW 23℃; LW 18℃; kushtet e ambientit: 35°CDB","(2) - Ftohje: EW 23℃; LW 18℃; kushtet e ambientit: 35°CDB","(2) - Ftohje: EW 23℃; LW 18℃; kushtet e ambientit: 35°CDB"]
["","","","","","(3) - Kushti: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Kushti: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Kushti: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Kushti: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Kushti: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Kushti: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Kushti: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Kushti: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(5) - Sipas EN14825","(5) - Sipas EN14825","(5) - Sipas EN14825","(5) - Sipas EN14825"]
["","","","","","(6) - Në varësi të regjimit të përdorimit, referojuni manualit të instalimit.","(6) - Në varësi të regjimit të përdorimit, referojuni manualit të instalimit.","(6) - Në varësi të regjimit të përdorimit, referojuni manualit të instalimit.","(6) - Në varësi të regjimit të përdorimit, referojuni manualit të instalimit."]
["","","","","","(7) - Për më shumë detaje, shihni skicën e diapazonit të funksionimit","(7) - Për më shumë detaje, shihni skicën e diapazonit të funksionimit","(7) - Për më shumë detaje, shihni skicën e diapazonit të funksionimit","(7) - Për më shumë detaje, shihni skicën e diapazonit të funksionimit"]