{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":69,"n_cols":8,"rows_kept":69,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXT-ATV3L"]
[]
[]
[]
[]
["","","","","","FWXT10ABTV3L","FWXT15ABTV3L","FWXT20ABTV3L"]
["Kapaciteti i ftohjes","7/12°C","","Min.","kW","0.49","0.62","0.70"]
["","","","Med.","kW","0.88","1.08","1.21"]
["","","","Maks.","kW","1.24","1.61","1.94"]
["Kapaciteti i ndjeshëm i ftohjes","7/12°C","","Min.","kW","0.37","0.52","0.57"]
["","","","Med.","kW","0.70","0.86","1.02"]
["","","","Maks.","kW","0.98","1.27","1.52"]
["Kapaciteti i ngrohjes","45/40°C","","Min.","kW","0.55","0.79","0.74"]
["","","","Med.","kW","1.00","1.36","1.55"]
["","","","Maks.","kW","1.50","2.01","2.13"]
["Fuqia në hyrje","Min.","","","kW","0.01","0.01","0.01"]
["","Med.","","","kW","0.01","0.01","0.01"]
["","Maks.","","","kW","0.02","0.02","0.03"]
["Shpejtësia e ventilatorit","Min.","","","rpm","680.00","680","680.00"]
["","Med.","","","rpm","1100.00","1100","1100.00"]
["","Maks.","","","rpm","1500.00","1500","1500.00"]
["Veshja e jashtme","Ngjyra","","","","RAL 9003","RAL 9003","RAL 9003"]
["","Materiali","","","","Fletë metalike","Fletë metalike","Fletë metalike"]
["Dimensionet","Njësia","","Lartësia","mm","335","335","335"]
["","","","Gjerësia","mm","902","1102","1302"]
["","","","Thellësia","mm","128","128","128"]
["","Njësia e ambalazhuar","","Lartësia","mm","490","490","490"]
["","","","Gjerësia","mm","1030","1230","1430"]
["","","","Thellësia","mm","210","210","210"]
["Pesha","Njësia","","","kg","14","16","19"]
["","Njësia e ambalazhuar","","","kg","15","17","20"]
["Ambalazhimi","Materiali","","","","Karton","Karton","Karton"]
["","Pesha","","","kg","1","1","1"]
["Shkëmbyesi i nxehtësisë","Sasia","","","","1","1","1"]
["","Vëllimi i bobinës së brendshme","","","l","0.5","0.61","0.77"]
["","Ngarkesa","","Presioni i funksionimit","bar","10","10","10"]
["Qarku i ujit","Diametri i lidhjeve të tubacioneve","","","in","3/4","3/4","3/4"]
["","Materiali i tubacionit","","","","BAKËR","BAKËR","BAKËR"]
["","Presioni","Ngrohje","Maks.","bar","10","10","10"]
["Qarku i ujit - rënia e presionit të ujit","Ngrohje","45/40°C","Min.","kPa","5.10","4.81","6.00"]
["","","","Med.","kPa","12.00","6.30","6.40"]
["","","","Maks.","kPa","16.30","7.20","8.10"]
["","Ftohje","7/12°C","Min.","kPa","4.80","4.70","5.50"]
["","","","Med.","kPa","10.50","5.60","5.40"]
["","","","Maks.","kPa","11.70","5.10","5.30"]
["Qarku i ujit - norma e qarkullimit të ujit","Ngrohje","45/40°C","Min.","kg/h","100.00","140","150.00"]
["","","","Med.","kg/h","170.00","240","300.00"]
["","","","Maks.","kg/h","260.00","350","420.00"]
["","Ftohje","7/12°C","Min.","kg/h","80.00","110","120.00"]
["","","","Med.","kg/h","150.00","190","210.00"]
["","","","Maks.","kg/h","210.00","280","330.00"]
["Niveli i fuqisë së zhurmës","Min.","","","dBA","35","36","37"]
["","Med.","","","dBA","46","47","48"]
["","Maks.","","","dBA","53.0","54","55.0"]
["Diapazoni i funksionimit","Ngrohje","Ana e ujit","Min.","°C","30","30","30"]
["","","","Maks.","°C","85","85","85"]
["","Ftohje","Ana e ujit","Min.","°C","5","5","5"]
["","","","Maks.","°C","18","18","18"]
["","Instalimi i brendshëm","Ambienti","Min.","°CDB","0","0","0"]
["","","","Maks.","°CDB","45","45","45"]
["Sistemet e kontrollit","Telekomandë me rreze infra të kuqe","","","","Për FWXT-ATV3(C)(CL)","Për FWXT-ATV3(C)(CL)","Për FWXT-ATV3(C)(CL)"]
["","Integruar në njësinë e brendshme","","","","Po","Po","Po"]
["Furnizimi me energji","Faza","","","","1~","1~","1~"]
["","Frekuenca","","","Hz","50","50","50"]
["","Tensioni","","","V","230","230","230"]
["Konsumi i energjisë elektrike","Maks.","","","W","19","20","29"]
["","Gatishmëria","","","W","3","4","5"]
["Rryma","Rryma maksimale e funksionimit","","Ngrohje","A","0.16","0.18","0.24"]
["","Rryma maksimale gjatë punës","","Ftohja","A","0.16","0.18","0.24"]